## S10a.Interruptions
[15 empty] | Company Name | Buller Electricity Limited
[15 empty] | For Year Ended | 2025-03-31
SCHEDULE 10a: REPORT ON INTERRUPTIONS
This schedule requires raw interruption data for the disclosure year. SAIDI and SAIFI is to be recorded using the multi-count approach.Where multiple feeders are affected, the interruption record is to be split into multiple interruptions, ie, one interruption record per feeder. This information is part of audited disclosure information (as defined in section 1.4 of this ID determination), and so is subject to the assurance report required by section 2.8.
sch ref
7 | 10a(i): Raw interruption data
8 |  | Interruption identifier | Circuit location | Sub-network (where applicable) | Feeder(s) affected by interruption | Start date (dd/mm/yyyy) | Start time (hh:mm:ss) | End date (dd/mm/yyyy) | End time (hh:mm:ss) | SAIDI value | SAIFI value | Number of ICPs interrupted | ICP interruption minutes | Planned or unplanned interruption (Class B or C) | Cause | Any explanation to help clarify the context of the interruption, including what the cause is if recorded as 'Other cause'
9 |  | OR-10022 | Mt Rochfort, Section 6080, ABS135 - F66 |  | 28-WHA | 2024-04-03 | 9:01 | 2024-04-03 | 12:47 | 0.091591 | 0.00040527 | 2 | 226 | BEL Planned (Class B) | Planned Outage | Replace 11kV Pole
10 |  | OR-10336 | Bulls Road, Cape Foulwind |  | 20-ADD | 2024-04-03 | 10:04 | 2024-04-03 | 11:57 | 0.068693 | 0.0006079 | 3 | 113 | BEL Planned (Class B) | Planned Outage | REPLACE STAY WIRE
11 |  | OR-11133 | Seddonville, Section 7260 , ABS56 - EOL |  | 42-SED | 2024-04-22 | 9:10 | 2024-04-22 | 11:51 | 1.7291 | 0.01074 | 53 | 161 | BEL Planned (Class B) | Planned Outage | Remove Trees
12 |  | OR-10088 | Between Deadmans Creek & Waimangaroa |  | 28-WHA | 2024-04-23 | 9:04 | 2024-04-23 | 15:29 | 1.0008 | 0.0026342 | 13 | 385 | BEL Planned (Class B) | Planned Outage | Replace 33kV CCT2 Arms & Straighten Poles
13 |  | OR-10107 | Little Wanganui, Section 11240, F40 - EOL |  | 60-LIT | 2024-04-24 | 9:06 | 2024-04-24 | 13:04 | 0.19291 | 0.00081054 | 4 | 238 | BEL Planned (Class B) | Planned Outage | Fell trees around powerlines
14 |  | OR-10093 | Wangapeka Road, Little Wanganui |  | 60-LIT | 2024-04-25 | 13:01 | 2024-04-25 | 21:15 | 3.2734 | 0.013779 | 68 | 494 | BEL Unplanned (Class C) | Defective Equipment | FAULT - CRACKED 11KV PIN
15 |  | OR-10098 | Kohaihai Road, Karamea |  | 62-KAR | 2024-04-29 | 9:00 | 2024-04-29 | 13:00 | 0.27558 | 0.0042553 | 21 | 240 | BEL Unplanned (Class C) | Defective Equipment | Broken jumper 11kV
16 |  | OR-10063 | Karamea, Section 9060, ABS77 - EOL |  | 62-KAR | 2024-04-30 | 9:00 | 2024-04-30 | 14:23 | 2.8798 | 0.0089159 | 44 | 323 | BEL Planned (Class B) | Planned Outage | Trim & fell trees
17 |  | OR-10123 | Whareatea feeder |  | 26-DOM, 28-WHA | 2024-05-02 | 6:30 | 2024-05-02 | 8:24 | 2.7413 | 0.12948 | 639 | 114 | BEL Unplanned (Class C) | Unknown | FAULT 282 TRIPPED
18 |  | OR-10132 | Cape Foulwind |  | 20-ADD | 2024-05-02 | 8:36 | 2024-05-02 | 13:44 | 0.062411 | 0.00020263 | 1 | 308 | BEL Planned (Class B) | Planned Outage | Install 11kV term arms, disconnect 11kV span. Dig in stay anchors
19 |  | OR-10136 | Golf Links Road, Carters Beach |  | 20-ADD | 2024-05-03 | 11:09 | 2024-05-03 | 11:58 | 1.0028 | 0.020466 | 101 | 49 | BEL Unplanned (Class C) | Defective Equipment | FAULT-BROKEN 11KV PREFORM
20 |  | OR-10159 | 8175 TOTARA ROAD CHARLESTON |  | 20-ADD | 2024-05-03 | 11:00 | 2024-05-03 | 12:00 | 0.012158 | 0.00020263 | 1 | 60 | BEL Unplanned (Class C) | Unknown | REPLACE BLOWN HV FUSE
21 |  | OR-10156 | Waimea Terrace Drive, Westport |  | 20-ADD | 2024-05-06 | 9:01 | 2024-05-06 | 14:39 | 0.95887 | 0.0028369 | 14 | 338 | BEL Planned (Class B) | Planned Outage | Replace 11kV S730
22 |  | OR-10202 | Utopia Road, Westport |  | 28-WHA | 2024-05-09 | 8:33 | 2024-05-09 | 15:29 | 6.6594 | 0.016008 | 79 | 416 | BEL Planned (Class B) | Planned Outage | Replace poles, conductor and subs
23 |  | OR-10058 | Little Wanganui |  | 60-LIT | 2024-05-15 | 9:39 | 2024-05-15 | 15:38 | 8.875 | 0.024721 | 122 | 359 | BEL Planned (Class B) | Planned Outage | Remove branches overhanging powerlines, Fell trees at Tidal Creek
24 |  | OR-10128 | Cape Foulwind |  | 20-ADD | 2024-05-23 | 9:06 | 2024-05-23 | 16:02 | 5.3106 | 0.012766 | 63 | 416 | BEL Planned (Class B) | Planned Outage | INSTALL 11KV POLES AND GENERAL LINE WORK
25 |  | OR-10209 | Cape Foulwind Road, Westport |  | 20-ADD | 2024-05-27 | 9:00 | 2024-05-27 | 15:43 | 3.8381 | 0.0095238 | 47 | 403 | BEL Planned (Class B) | Planned Outage | INSTALL 11KV POLES & GENERAL LINE WORK
26 |  | OR-10337 | Lower Buller Gorge |  | 20-ADD | 2024-06-04 | 10:30 | 2024-06-04 | 11:30 | 0.012158 | 0.00020263 | 1 | 60 | BEL Unplanned (Class C) | Unknown | REPLACE BLOWN HV FUSE
27 |  | OR-10338 | MT ROCHFORT |  | 28-WHA | 2024-06-04 | 19:13 | 2024-06-04 | 19:40 | 0.010942 | 0.00040527 | 2 | 27 | BEL Unplanned (Class C) | Unknown | REPLACE HV FUSES
28 |  | OR-10176 | Buller Road, Westport |  | 20-ADD | 2024-06-06 | 9:03 | 2024-06-06 | 14:24 | 3.6539 | 0.01155 | 57 | 321 | BEL Planned (Class B) | Planned Outage | Replace two inline 11kV poles with excavator
29 |  | OR-10252 | Hector |  | 36-NGK/KON, 42-SED | 2024-06-11 | 8:31 | 2024-06-11 | 14:30 | 10.2389 | 0.032219 | 159 | 359 | BEL Planned (Class B) | Planned Outage | REPLACE 33/11 KV POLE, CONNECT 11KV SPURLINE & REMOVE SEC 5
30 |  | OR-10199 | Stephen Road, Westport |  | 28-WHA | 2024-06-13 | 9:01 | 2024-06-13 | 14:57 | 6.4559 | 0.018237 | 90 | 356 | BEL Planned (Class B) | Planned Outage | REPLACE DOUBLE POLE STRUCTURE WITH SINGLE BUSCK & REMOVE ABS 38
31 |  | OR-10333 | 109 NINE MILE ROAD (OLD PACKING PLANT) |  | 28-WHA | 2024-06-16 | 13:30 | 2024-06-16 | 14:30 | 0.048632 | 0.00081054 | 4 | 60 | BEL Unplanned (Class C) | Lightning | REPLACE BLOWN HV FUSES
32 |  | OR-10331 | MARS BEACH |  | 20-ADD | 2024-06-19 | 18:00 | 2024-06-19 | 18:30 | 0.006079 | 0.00020263 | 1 | 30 | BEL Unplanned (Class C) | Unknown | REPLACE BLOWN HV FUSES
33 |  | OR-10332 | SHADICK AVE CARTERS BEACH |  | 20-ADD | 2024-06-19 | 10:21 | 2024-06-19 | 13:30 | 0.36657 | 0.0042553 | 21 | 189 | BEL Unplanned (Class C) | Unknown | REPLACE BLOWN POLE FUSES
34 |  | OR-10230 | ST HELENS, MOKIHINUI |  | 42-SED | 2024-06-20 | 9:04 | 2024-06-20 | 12:19 | 0.23708 | 0.0012158 | 6 | 195 | BEL Planned (Class B) | Planned Outage | REPLACE LV POLE, INSTALL STAY AND BARRIER
35 |  | OR-10326 | Nine Mile Road, Westport |  | 28-WHA | 2024-06-21 | 7:53 | 2024-06-21 | 8:41 | 0.15562 | 0.0032421 | 16 | 48 | BEL Unplanned (Class C) | Unknown | REPLACE 2 X BLOWN HV FUSES
36 |  | OR-10329 | LITTLE Wanganui |  | 60-LIT | 2024-06-23 | 10:00 | 2024-06-23 | 12:30 | 1.6717 | 0.011145 | 55 | 150 | BEL Unplanned (Class C) | Unknown | REPLACE BLOWN HV FUSES
37 |  | OR-10279 | POLE 1804 BETWEEN MARTINS CREEK & BULLER BRIDGE |  | 20-ADD | 2024-06-24 | 0:57 | 2024-06-24 | 5:45 | 0.7003 | 0.0024316 | 12 | 288 | BEL Unplanned (Class C) | Third Party Interference | CAR VS POLE MARTINS BEND
38 |  | OR-10236 | Cains Road, Birchfield |  | 40-WAI | 2024-06-26 | 9:05 | 2024-06-26 | 14:03 | 0.30193 | 0.0010132 | 5 | 298 | BEL Planned (Class B) | Planned Outage | RESAG 11KV CONDUCTOR AND GENERAL MAINTENANCE
39 |  | OR-10285 | Nikau Road, Hector |  | 42-SED | 2024-06-26 | 9:02 | 2024-06-26 | 10:21 | 0.080041 | 0.0010132 | 5 | 79 | BEL Planned (Class B) | Planned Outage | Replace 30kVA sub 661 & earth rods
40 |  | OR-10305 | Reedys Road, Westport |  | 28-WHA | 2024-06-27 | 9:03 | 2024-06-27 | 10:57 | 0.1617 | 0.0014184 | 7 | 114 | BEL Planned (Class B) | Planned Outage | REPLACE 11KV CROSSARMS
41 |  | OR-10299 | Utopia Road, Westport |  | 28-WHA | 2024-06-27 | 9:53 | 2024-06-27 | 11:18 | 0.034448 | 0.00040527 | 2 | 85 | BEL Planned (Class B) | Planned Outage | REPLACE DDOS & LIGHTNINING ARRESTORS
42 |  | OR-10264 | Fox River |  | 20-ADD | 2024-07-04 | 9:00 | 2024-07-04 | 14:55 | 2.9909 | 0.0085106 | 42 | 355 | BEL Planned (Class B) | Planned Outage | Replace poles and general linework
43 |  | OR-10242 | Karamea |  | 62-KAR | 2024-07-10 | 11:36 | 2024-07-10 | 12:41 | 0.026342 | 0.00040527 | 2 | 65 | BEL Planned (Class B) | Planned Outage | REPLACE SUB 396
44 |  | OR-10271 | LITTLE WANGANUI |  | 60-LIT | 2024-07-11 | 9:00 | 2024-07-11 | 13:30 | 6.7295 | 0.024924 | 123 | 270 | BEL Planned (Class B) | Planned Outage | REPLACE POLES & 33KV INSULATORS & TRIM TREES
45 |  | OR-10370 | Fonblanque Street, Westport |  | 22-RUS | 2024-07-11 | 21:20 | 2024-07-11 | 22:42 | 0.016616 | 0.00020263 | 1 | 82 | BEL Planned (Class B) | Planned Outage | Tighten internal LV bushing SUB 474
46 |  | OR-10377 | Fairdown |  | 28-WHA | 2024-07-11 | 4:53 | 2024-07-11 | 15:20 | 6.8316 | 0.017629 | 87 | 627 | BEL Unplanned (Class C) | Unknown | CB1392 TRIP - REPLACE CROSSARMS AT POLE 50134
47 |  | OR-10248 | Karamea |  | 62-KAR | 2024-07-12 | 10:09 | 2024-07-12 | 11:18 | 0.097872 | 0.0014184 | 7 | 69 | BEL Planned (Class B) | Planned Outage | REPLACE SUB 411
48 |  | OR-10311 | Fairdown |  | 28-WHA | 2024-07-17 | 9:03 | 2024-07-17 | 13:30 | 4.707 | 0.017629 | 87 | 267 | BEL Planned (Class B) | Planned Outage | REPLACE 11KV CROSSARMS, INSTALL 11KV FUSES & NEW SUB
49 |  | OR-10382 | Oparara Road, Karamea |  | 62-KAR | 2024-07-19 | 9:01 | 2024-07-19 | 14:19 | 0.45106 | 0.0014184 | 7 | 318 | BEL Planned (Class B) | Planned Outage | REPLACE LV CROSSARMS, CONNECT NEW ABC TO SERVICE POLE
50 |  | OR-10459 | Shaddock ave, Carters Beach |  | 20-ADD | 2024-07-25 | 8:50 | 2024-07-25 | 9:30 | 0.17021 | 0.0042553 | 21 | 40 | BEL Unplanned (Class C) | Unknown | 2X BLOWN HT FUSES
51 |  | OR-10358 | McKenna Road, Westport |  | 28-WHA | 2024-07-30 | 8:15 | 2024-07-30 | 14:43 | 5.6608 | 0.01459 | 72 | 388 | BEL Planned (Class B) | Planned Outage | Reconductor 11kV & General Lines Maintenance
52 |  | OR-10441 | KARAMEA BLUFF |  | 36-NGK/KON | 2024-08-09 | 9:00 | 2024-08-09 | 14:39 | 0.20608 | 0.0006079 | 3 | 339 | BEL Planned (Class B) | Planned Outage | INSTALL LINKS AT POLE 70418, TRACK & TREE CUTTING
53 |  | OR-10464 | Peel Street, Westport |  | 23-DER | 2024-08-20 | 8:30 | 2024-08-20 | 16:12 | 16.738 | 0.036677 | 181 | 462 | BEL Planned (Class B) | Planned Outage | REPLACE SUB 158 WITH GROUNDMOUNT
54 |  | OR-10531 | 708 NIKAU ROAD |  | 42-SED | 2024-08-27 | 5:57 | 2024-08-27 | 12:47 | 0.24924 | 0.0006079 | 3 | 410 | BEL Unplanned (Class C) | Lightning | REPLACE 3 HV FUSES SUPPLYING SUB 321
55 |  | OR-10530 | MT ROCHFORT |  | 28-WHA | 2024-08-27 | 5:05 | 2024-08-27 | 12:25 | 0.17832 | 0.00040527 | 2 | 440 | BEL Unplanned (Class C) | Lightning | REPLACE BLOWN FUSES 57
56 |  | OR-10597 | Denniston |  | 28-WHA | 2024-08-27 | 5:05 | 2024-08-27 | 12:00 | 0.58865 | 0.0014184 | 7 | 415 | BEL Unplanned (Class C) | Lightning | NO POWER FAULT
57 |  | OR-10472 | Mokihinui |  | 42-SED | 2024-08-29 | 9:07 | 2024-08-29 | 14:43 | 3.5404 | 0.010537 | 52 | 336 | BEL Planned (Class B) | Planned Outage | REPLACE 11KV POLE
58 |  | OR-10551 | 8860 SH6 |  | 20-ADD | 2024-08-30 | 9:30 | 2024-08-30 | 11:00 | 0.036474 | 0.00040527 | 2 | 90 | BEL Unplanned (Class C) | Lightning | REPLACE BLOWN HV FUSE
59 |  | OR-10554 | 114 FLAXMILL ROAD, KARAMEA |  | 62-KAR | 2024-08-30 | 0:00 | 2024-08-30 | 10:30 | 0.12766 | 0.00020263 | 1 | 630 | BEL Unplanned (Class C) | Lightning | REPLACE BLOWN HV FUSE
60 |  | OR-10552 | 23/153 ALMA ROAD |  | 20-ADD | 2024-08-30 | 7:30 | 2024-08-30 | 10:00 | 0.030395 | 0.00020263 | 1 | 150 | BEL Unplanned (Class C) | Lightning | REPLACE BLOWN HV FUSE
61 |  | OR-10553 | Linehams Road, Karamea |  | 62-KAR | 2024-08-30 | 7:30 | 2024-08-30 | 11:30 | 0.048632 | 0.00020263 | 1 | 240 | BEL Unplanned (Class C) | Lightning | REPLACE BLOWN HV FUSE
62 |  | OR-10539 | MT ROCHFORT |  | 28-WHA | 2024-08-30 | 7:30 | 2024-08-30 | 14:00 | 0.18703 | 0.00081054 | 4 | 390 | BEL Unplanned (Class C) | Lightning | REPAIR BROKEN JUMPER FUSES 57
63 |  | OR-10544 | Fairdown |  | 20-ADD, 28-WHA | 2024-08-31 | 18:37 | 2024-09-01 | 18:00 | 5.2904 | 0.025329 | 125 | 1403 | BEL Unplanned (Class C) | Lightning | Broken 33kv pin on pole 50135
64 |  | OR-10545 | Caledonian Road, Westport |  | 28-WHA | 2024-08-31 | 23:04 | 2024-09-01 | 13:00 | 0.1694 | 0.00020263 | 1 | 836 | BEL Unplanned (Class C) | Lightning | REPLACE SUB 517 CALEDONIAN ROAD (BEAR HUNTER)
65 |  | OR-10502 | Cape Foulwind |  | 20-ADD | 2024-09-04 | 9:03 | 2024-09-04 | 16:04 | 1.9465 | 0.0046606 | 23 | 421 | BEL Planned (Class B) | Planned Outage | REMOVE ABS 11 & 12 - REPLACE ABS 13
66 |  | OR-10611 | Nine Mile Road, Westport |  | 28-WHA | 2024-09-05 | 20:00 | 2024-09-05 | 21:45 | 0.34043 | 0.0032421 | 16 | 105 | BEL Unplanned (Class C) | Unknown | Blown HV Fuses
67 |  | OR-10601 | Tauranga Bay Road, Cape Foulwind |  | 20-ADD | 2024-09-08 | 21:55 | 2024-09-08 | 23:55 | 0.19453 | 0.0016211 | 8 | 120 | BEL Unplanned (Class C) | Defective Equipment | REPAIR BURNT OUT CONNECTOR ON 11KV CABLE
68 |  | OR-10594 | NORTH BEACH, KARAMEA |  | 62-KAR | 2024-09-11 | 9:04 | 2024-09-11 | 14:50 | 1.4723 | 0.0042553 | 21 | 346 | BEL Planned (Class B) | Planned Outage | REPLACE POLES, CROSSARMS AND CONDUCTOR
69 |  | OR-10514 | Flaxmill Road, Karamea |  | 62-KAR | 2024-09-12 | 9:04 | 2024-09-12 | 14:14 | 0.062817 | 0.00020263 | 1 | 310 | BEL Planned (Class B) | Planned Outage | REPLACE 11KV TX POLE
70 |  | OR-10616 | Karamea |  | 62-KAR | 2024-09-15 | 8:40 | 2024-09-15 | 12:39 | 0.04843 | 0.00020263 | 1 | 239 | BEL Unplanned (Class C) | Defective Equipment | Replace Sub 442
71 |  | OR-10618 | Schadick Avenue, Carters Beach |  | 20-ADD | 2024-09-16 | 7:30 | 2024-09-16 | 9:15 | 0.44681 | 0.0042553 | 21 | 105 | BEL Unplanned (Class C) | Wildlife | Swan hit lines
72 |  | OR-10680 | NORTH BEACH, KARAMEA |  | 62-KAR | 2024-09-18 | 9:02 | 2024-09-18 | 14:35 | 1.417 | 0.0042553 | 21 | 333 | BEL Planned (Class B) | Planned Outage | REPLACE POLES, CROSSARMS AND CONDUCTOR
73 |  | OR-10645 | CNR SHADDICK AVE, GOLF LINKS RD |  | 20-ADD | 2024-09-19 | 3:45 | 2024-09-19 | 4:30 | 0.0091185 | 0.00020263 | 1 | 45 | BEL Unplanned (Class C) | Wildlife | PART POWER WESTREEF PUMP STATION
74 |  | OR-10556 | NORTH BEACH KARAMEA |  | 62-KAR | 2024-09-20 | 9:00 | 2024-09-20 | 15:22 | 1.6255 | 0.0042553 | 21 | 382 | BEL Planned (Class B) | Planned Outage | RECONDUCTOR 11KV
75 |  | OR-10317 | Powerhouse Road, Fairdown |  | 28-WHA | 2024-09-26 | 9:13 | 2024-09-26 | 10:58 | 0.2766 | 0.0026342 | 13 | 105 | BEL Planned (Class B) | Planned Outage | REPLACE SUB 568
76 |  | OR-10647 | KONGAHU STRAIGHT |  | 60-LIT | 2024-09-28 | 3:30 | 2024-09-28 | 6:30 | 0.072948 | 0.00040527 | 2 | 180 | BEL Unplanned (Class C) | Wildlife | NO POWER- SWAN HIT LINE
77 |  | OR-10669 | Domain Road, Cape Foulwind |  | 20-ADD | 2024-10-10 | 9:03 | 2024-10-10 | 14:44 | 0.89828 | 0.0026342 | 13 | 341 | BEL Planned (Class B) | Planned Outage | Domain rd LV upgrade
78 |  | OR-10677 | Domain Road, Cape Foulwind |  | 20-ADD | 2024-10-11 | 9:20 | 2024-10-11 | 10:10 | 0.34448 | 0.0068896 | 34 | 50 | BEL Unplanned (Class C) | Defective Equipment | SUB CHECK
79 |  | OR-10656 | Golf Course Road, Karamea |  | 62-KAR | 2024-10-16 | 9:43 | 2024-10-16 | 14:14 | 0.3844 | 0.0014184 | 7 | 271 | BEL Planned (Class B) | Planned Outage | Replace 11kV TX. Remove OH LV & hardware & install new cable
80 |  | OR-10637 | McKenna Road, Westport |  | 28-WHA | 2024-10-22 | 9:08 | 2024-10-22 | 12:24 | 1.9461 | 0.0099291 | 49 | 196 | BEL Planned (Class B) | Planned Outage | Replace 11kv jumpers
81 |  | OR-10697 | Pines Corner |  | 28-WHA | 2024-10-22 | 17:45 | 2024-10-22 | 23:31 | 6.5905 | 0.019048 | 94 | 346 | BEL Unplanned (Class C) | Third Party Interference | De-Energise Power for crane to lift rolled Truck & Crusher
82 |  | OR-10727 | KERRS CROSSING, GRANITY |  | 40-WAI | 2024-10-25 | 7:40 | 2024-10-25 | 8:30 | 0.020263 | 0.00040527 | 2 | 50 | BEL Unplanned (Class C) | Lightning | REPLACE 2 X BLOWN HV FUSES
83 |  | OR-10642 | Tauranga Bay Road, Cape Foulwind |  | 20-ADD | 2024-10-29 | 8:34 | 2024-10-29 | 16:52 | 5.4241 | 0.084296 | 416 | 498 | BEL Planned (Class B) | Planned Outage | General Line work and maintenance
84 |  | OR-10665 | Cape Foulwind |  | 20-ADD | 2024-10-31 | 8:30 | 2024-10-31 | 15:14 | 0.88916 | 0.054306 | 268 | 404 | BEL Planned (Class B) | Planned Outage | RECONDUCTOR 11KV FROM POLE 1134 TO 1155
85 |  | OR-10710 | Cape Foulwind |  | 20-ADD | 2024-11-27 | 8:29 | 2024-11-27 | 15:50 | 4.894 | 0.064843 | 320 | 441 | BEL Planned (Class B) | Planned Outage | RECONDUCTOR 11KV SEC 700
86 |  | OR-10738 | COAST ROAD |  | 20-ADD | 2024-12-04 | 8:30 | 2024-12-04 | 15:00 | 3.8723 | 0.0099291 | 49 | 390 | BEL Planned (Class B) | Planned Outage | REPLACE 3 X 11KV POLES
87 |  | OR-10801 | Granite Creek Road, Karamea |  | 62-KAR | 2024-12-10 | 14:30 | 2024-12-10 | 17:30 | 0.36474 | 0.0020263 | 10 | 180 | BEL Unplanned (Class C) | Wildlife | NO POWER GRANITE CREEK RD
88 |  | OR-10798 | Little Wanganui |  | 60-LIT | 2024-12-13 | 19:00 | 2024-12-13 | 23:10 | 1.9141 | 0.024924 | 123 | 250 | BEL Unplanned (Class C) | Defective Equipment | Replace DDO's Supplying Sub 632 Little Wanganui
89 |  | OR-10806 | 9225 SH6 |  | 20-ADD | 2024-12-16 | 6:00 | 2024-12-16 | 8:00 | 0.048632 | 0.00040527 | 2 | 120 | BEL Unplanned (Class C) | Lightning | REPLACE BLOWN DDO FUSE
90 |  | OR-10767 | Darkies Terrace Road, Charleston |  | 20-ADD | 2024-12-17 | 9:00 | 2024-12-17 | 12:35 | 0.1307 | 0.0006079 | 3 | 215 | BEL Planned (Class B) | Planned Outage | REMOVE FUSES 289, INSTALL SUB 867
91 |  | OR-10816 | SHADICK DRIVE CARTERS BEACH |  | 20-ADD | 2024-12-20 | 22:00 | 2024-12-20 | 22:45 | 0.19149 | 0.0042553 | 21 | 45 | BEL Unplanned (Class C) | Defective Equipment | BROKEN HV FUSE LINK
92 |  | OR-10815 | Stephen Road, Westport |  | 28-WHA | 2024-12-30 | 12:30 | 2024-12-30 | 14:00 | 0.036474 | 0.00040527 | 2 | 90 | BEL Unplanned (Class C) | Wildlife | BIRD STRIKE, 2 X BLOWN HV FUSES
93 |  | OR-10812 | Granite Creek Road, Karamea |  | 62-KAR | 2025-01-01 | 14:00 | 2025-01-01 | 15:30 | 0.18237 | 0.0020263 | 10 | 90 | BEL Unplanned (Class C) | Unknown | BLOWN HV FUSES
94 |  | OR-10751 | Birchfield |  | 36-NGK/KON, 38-STK, 40-WAI, 42-SED | 2025-01-03 | 8:20 | 2025-01-03 | 13:55 | 5.6322 | 0.21783 | 1075 | 335 | BEL Planned (Class B) | Planned Outage | 33KV ROB/NGK CCT CROSSINGS
95 |  | OR-10923 | Millerton |  | 40-WAI | 2025-01-29 | 9:45 | 2025-01-29 | 13:24 | 1.3757 | 0.0062817 | 31 | 219 | BEL Unplanned (Class C) | Unknown | REC 22 TRIPPED
96 |  | OR-10933 | Karamea |  | 62-KAR | 2025-01-31 | 14:25 | 2025-01-31 | 16:25 | 1.1185 | 0.0093212 | 46 | 120 | BEL Unplanned (Class C) | Human Error | RECLOSER 11 TRIPPED A-C-E FAULT
97 |  | OR-10936 | Oparara Road, Karamea |  | 62-KAR | 2025-02-04 | 3:08 | 2025-02-04 | 9:30 | 3.6999 | 0.011348 | 56 | 382 | BEL Unplanned (Class C) | Vegetation | REC 21 Tripped
98 |  | OR-10955 | BUNNINGS ROAD |  | 20-ADD | 2025-02-06 | 20:30 | 2025-02-06 | 21:00 | 0.018237 | 0.0006079 | 3 | 30 | BEL Unplanned (Class C) | Wildlife | BIRD STRIKE
99 |  | OR-10954 | Granite Creek Road, Karamea |  | 62-KAR | 2025-02-07 | 22:00 | 2025-02-07 | 23:30 | 0.18237 | 0.0020263 | 10 | 90 | BEL Unplanned (Class C) | Wildlife | 2X Blown HV fuses
100 |  | OR-10960 | Oparara Road, Karamea |  | 62-KAR | 2025-02-12 | 9:00 | 2025-02-12 | 13:15 | 0.15502 | 0.0006079 | 3 | 255 | BEL Unplanned (Class C) | Defective Equipment | HV FUSE DROPPED OUT (NOT BLOWN)
101 |  | OR-10866 | KAWATIRI PLACE |  | 26-DOM | 2025-02-17 | 9:00 | 2025-02-17 | 9:09 | 0.093009 | 0.010334 | 51 | 9 | BEL Planned (Class B) | Planned Outage | DE ENERGISE SUB 640 TO CHANGE TAP POSITION
102 |  | OR-10831 | Ngakawau |  | 40-WAI | 2025-02-18 | 9:03 | 2025-02-18 | 15:54 | 0.58298 | 0.0014184 | 7 | 411 | BEL Planned (Class B) | Planned Outage | UNDER GROUND TYLER ROAD NGAKAWAU
103 |  | OR-10819 | Ngakawau |  | 42-SED | 2025-02-20 | 9:27 | 2025-02-20 | 15:37 | 7.8363 | 0.08227 | 406 | 370 | BEL Planned (Class B) | Planned Outage | 11KV MAINTENANCE NGAKAWAU
104 |  | OR-10981 | Palmerston Street, Westport |  | 22-RUS | 2025-02-21 | 14:30 | 2025-02-21 | 16:00 | 0.40122 | 0.004458 | 22 | 90 | BEL Unplanned (Class C) | Defective Equipment | Part Power - Shops on Palmerston Street
105 |  | OR-10825 | Ngakawau |  | 42-SED | 2025-02-25 | 9:01 | 2025-02-25 | 15:46 | 8.1759 | 0.08227 | 406 | 405 | BEL Planned (Class B) | Planned Outage | 11KV MAINTENANCE NGAKAWAU
106 |  | OR-10984 | 438 Okari Road, Cape Foulwind Sub34 |  | 20-ADD | 2025-02-28 | 12:30 | 2025-02-28 | 14:00 | 0.018237 | 0.00020263 | 1 | 90 | BEL Unplanned (Class C) | Defective Equipment | Part Power
107 |  | OR-10985 | Lighthouse Road, Cape Foulwind |  | 20-ADD | 2025-03-03 | 8:30 | 2025-03-03 | 9:30 | 0.44985 | 0.0074975 | 37 | 60 | BEL Unplanned (Class C) | Defective Equipment | Part Power - Lighthouse Road
108 |  | OR-11010 | Millerton |  | 40-WAI | 2025-03-08 | 6:40 | 2025-03-08 | 8:55 | 0.84802 | 0.0062817 | 31 | 135 | BEL Unplanned (Class C) | Unknown | Rec 22 tripped - No comms
109 |  | OR-10908 | Okari Road, Cape Foulwind |  | 20-ADD | 2025-03-11 | 8:21 | 2025-03-11 | 15:31 | 1.6326 | 0.067072 | 331 | 430 | BEL Planned (Class B) | Planned Outage | REPLACE DOUBLE STRUCTURE
110 |  | OR-11014 | CB 1332 to ABS126 |  | 34-ROB/NGK-CCT2 | 2025-03-18 | 8:37 | 2025-03-18 | 14:49 | 0.0034448 | 0.00040527 | 2 | 372 | BEL Planned (Class B) | Planned Outage | Trim and fell trees around powerlines
111 |  | OR-11074 | Bulls Road, Cape Foulwind |  | 20-ADD | 2025-03-25 | 8:37 | 2025-03-25 | 15:29 | 1.1664 | 0.0028369 | 14 | 412 | BEL Planned (Class B) | Planned Outage | REPLACE 2X POLES
112 |  | OR-11050 | KARAMEA BLUFF |  | 36-NGK/KON | 2025-03-31 | 8:19 | 2025-03-31 | 14:46 | 0.23526 | 0.0006079 | 3 | 387 | BEL Planned (Class B) | Planned Outage | FLY IN GRAVEL TO POLE SITES, REPLACE 1 X POLE
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
161
162
163
164
165
166
167
168
169
170
171
172
173
174
175
176
177
178
179
180
181
182
183
184
185
186
187
188
189
190
191
192
193
194
195
196
197
198
199
200
201
202
203
204
205
206
207
208
¹ Extend table as necessary to disclose information for all individual interruptions